{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["NG Start-Up Sheet","Dual Fuel Addendum"],"not_rendered":{"charts":0,"images":4,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"NG Start-Up Sheet","index":0,"n_rows":53,"n_cols":30,"rows_kept":53,"cut":false,"hidden":false,"merged":[[8,22,8,23],[9,22,9,23],[10,22,10,23],[10,13,10,20],[1,1,1,2],[8,13,8,15],[5,22,6,27],[3,24,3,26],[2,24,2,26],[3,15,3,16],[1,22,1,23],[2,22,2,23],[3,22,3,23],[1,24,1,27],[18,13,18,14],[19,13,19,14],[3,1,3,2],[2,1,2,2],[1,3,1,6],[3,3,3,6],[1,8,1,9],[3,11,3,12],[2,3,2,8],[11,1,11,3],[9,1,9,6],[14,13,14,14],[13,13,13,14],[12,13,12,14],[5,13,5,20],[7,13,7,15],[46,1,46,8],[47,1,47,2],[10,1,10,3],[6,8,6,11],[7,8,8,9],[9,8,9,9],[27,1,27,14],[15,8,15,11],[25,1,25,14],[15,13,15,14],[10,8,10,9],[13,8,14,9],[38,12,38,13],[39,12,39,13],[5,1,6,6],[11,8,12,9],[51,21,52,28],[18,27,18,28],[17,13,17,14],[15,15,15,18],[16,13,16,14],[26,1,26,14],[29,1,29,6],[52,3,52,8],[36,28,36,30],[34,28,34,30],[35,28,35,30],[34,19,34,25],[35,19,35,25],[25,17,25,31],[33,12,33,14],[49,1,49,2],[50,1,50,2],[48,1,48,2],[47,21,49,28],[26,17,26,31],[27,17,27,31],[30,17,31,18],[34,17,34,18],[35,17,35,18],[36,17,36,18],[37,17,37,18],[38,19,38,25],[37,19,37,25],[36,19,36,25],[38,1,38,6],[39,2,39,5],[43,1,43,14],[44,1,44,14],[30,19,30,31],[31,19,31,31],[30,7,30,8],[35,7,35,8],[35,9,35,11],[36,9,36,11],[37,9,37,11],[40,12,40,13],[30,10,30,14],[40,19,44,31],[42,1,42,14],[31,12,31,14],[32,12,32,14],[11,22,11,27],[28,17,28,31],[19,27,19,28],[19,30,19,31],[17,22,17,32],[18,30,18,31]]}
[]
[null,"Project :",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Model:"]
[null,"Address:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Serial Number:"]
[null,"City:",null,null,null,null,null,null,null,null,null,"Province: ",null,null,"Postal Code:",null,null,null,null,null,null,null,"Start-up Date:"]
[]
[null,"OVERVIEW",null,null,null,null,null,null,"GAS SUPPLY",null,null,null,null,"WATER & ELECTRICAL",null,null,null,null,null,null,null,null,"COMBUSTION*",null,null,null,null,null,null,"SAFETIES TESTED"]
[null,null,null,null,null,null,null,null,"Inspect gas pipe, regulator and meter sizing."]
[null,null,null,null,null,null,null,null,"Is it sized correctly for the BTU/Hr requirement?",null,null,null,null,"Water Pipe Dia. (in.): ",null,null,null,null,null,null,null,null,null,null,"Valve 1 Low Fire:",null,"Valve 1 High Fire:",null,null,"High Limit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"System Water pH Level: ",null,null,null,null,null,null,null,null,"O2%",null,null,null,null,null,null,"Flow Swith "]
[null,"How many units are installed at this location? ",null,null,null,null,null,null,"Gas Pipe Dia. (in.):",null,null,null,null,null,null,null,null,null,null,null,null,null,"CO2%",null,null,null,null,null,null,"Low Pressure"]
[null,"Boiler(s):",null,null,null,null,null,null,"Equivalent Feet:",null,null,null,null,"Read and record",null,null,null,null,null,null,null,null,"CO ppm",null,null,null,null,null,null,"High Pressure"]
[null,"Water Heater(s):",null,null,null,null,null,null,"Is there an inlet gas lockup regulator on the supply?",null,null,null,null,null,null,"High Fire",null,null,"Low Fire",null,null,null,null,null,null,null,null,null,null,"LWCO"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Inlet Temp:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Flame Safe Guard"]
[null,null,null,null,null,null,null,null,"If Yes, is it 10 ft. upstream from the appliance? ",null,null,null,null,"Outlet Temp:",null,null,null,null,null,null,null,null,"Notes/Comments regarding safeties:",null,null,null,null,null,null,"Relief Valve"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Delta T:"]
[null,null,null,null,null,null,null,null,"Record in. of water column** ",null,null,null,null,"Pump Location:"]
[null,null,null,null,null,null,null,null,"Static Pressure:",null,null,null,null,"Pump Control:"]
[null,null,null,null,null,null,null,null," Pressure Drop @ Ignition:",null,null,null,null,"Supply Voltage:",null,null,null,"L1:",null,null,null,null,"CLEARANCES  Measure and record (inches) the service clearances from the nearest obstruction (min. 24\" required for service): "]
[null,null,null,null,null,null,null,null,"Hi-Fire Gas Pressure:",null,null,null,null,"Total Amp Draw:",null,null,null,"L2:",null,null,null,null,"Front:",null,null,null,"Left Side:",null,null,"Top:"]
[null,null,null,null,null,null,null,null,"Low-Fire Gas Pressure:",null,null,null,null,"Voltage Between N-G:",null,null,null,"L3:",null,null,null,null,"Rear:",null,null,null,"Right Side:"]
[]
[]
[]
[]
[]
[null,"Comments/Corrections needed for gas supply, water or electricity:",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Comments/Corrections need for service clearances:"]
[]
[]
[]
[null,"VENTING (Select the option being used):",null,null,null,null,null,"VENT TERMINATION"]
[null,null,null,null,null,null,null,null,null,null,"Record the following:",null,null,null,null,null,null,"General Job Notes:    "]
[null,null,null,null,null,null,null,null,null,null,null,"Vent Pressure \"w.c.:"]
[null,null,null,null,null,null,null,null,null,null,null,"Inlet Air Pressure \"w.c.: ",null,null,null,null,null," "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"START-UP PERFORMED BY: ",null,null,null,null,null,null,null,null,null,"Internal Use: "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Company:",null,null,null,null,null,null,null,null,null,"S/O #: "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Name:",null,null,null,null,null,null,null,null,null,"Routed:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Phone:",null,null,null,null,null,null,null,null,null,"Tech:"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"PK Certifcation #:  "]
[null,"Heat Exchanger condensate piped to:  ",null,null,null,null,null,null,null,null,null,"Total Eqv. Length (ft.):",null,null,null,null,null,null,"        TSSA#"]
[null,null," Air Inlet Diameter (in.):",null,null,null,null,null,null,null,null,"Flue Diameter (in.):"]
[null,null,null,null,null,"Air Inlet Material: ",null,null,null,null,null,"Flue Material: ",null,null,null,null,null,null,null,"This Startup Sheet is for use only by a qualified heating installer/service technician.  Refer to the Installation and Operation Manual for your reference.  Have this unit serviced/inspected by a qualified service technician, at least annually.  Failure to comply with the above could result in severe personal injury, death, or substantial property damage."]
[]
[null,"Comments/Corrections needed for vent, HEX, or air inlet piping:"]
[]
[]
[]
[null,"Send completed form to:"]
[null,"Email: ",null,"pkchtsupport@spx.com",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"* Note:  For Dual Fuel Models, please fill out the Dual Fuel Addendum worksheet in addition to this sheet. "]
[null,"Phone: ",null,"1 (570)-476-7261"]
[null,"Fax:",null,"1 (570)-476-7247"]
[null,"Mail:",null,"Service Dept. / Patterson-Kelley"]
[null,null,null,"155 Burson Street",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"** Note:  Gas Pressure Drop should be checked with Water Tube Manometer."]
[null,null,null,"East Stroudsburg, PA 18301"]

{"sheet":"Dual Fuel Addendum","index":1,"n_rows":17,"n_cols":21,"rows_kept":17,"cut":false,"hidden":false,"merged":[[13,11,18,15],[6,9,6,10],[12,4,12,7],[1,1,1,2],[2,1,2,2],[3,1,3,2],[1,18,1,19],[2,18,2,19],[3,18,3,19],[8,4,9,4],[10,4,11,4]]}
[]
[null,"Job Name:",null,{"$f":"'NG Start-Up Sheet'!D2","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Model:",null,{"$f":"'NG Start-Up Sheet'!Y2","v":0}]
[null,"Address:",null,{"$f":"'NG Start-Up Sheet'!D3","v":0},null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Serial Number:",null,{"$f":"'NG Start-Up Sheet'!Y3","v":0}]
[null,"City:",null,{"$f":"'NG Start-Up Sheet'!D4","v":0},null,null,null,null,null,null,null,"State:",{"$f":"'NG Start-Up Sheet'!M4","v":0},null,null,"Zip:",{"$f":"'NG Start-Up Sheet'!P4","v":0},null,"Start-up Date:",null,{"$f":"'NG Start-Up Sheet'!Y4","v":0}]
[]
[null,null,null,null,"GAS SUPPLY",null,null,null,null,"COMBUSTION"]
[null,null,null,null,"Gas Pipe Dia. (in.):",null,null,null,null,"Valve 1 Low Fire:",null,null,"Valve 1 High Fire:"]
[null,null,null,null,"Equivalent Feet:",null,null,null,null,"O2%"]
[null,null,null,null,"Is there an inlet gas lockup regulator on the supply?",null,null,null,null,"CO ppm"]
[null,null,null,null,null,null,null,null,null,"CO2%"]
[null,null,null,null,"If Yes, is it 10 ft. upstream from the appliance? "]
[]
[null,null,null,null,"Record in. of water column* -"]
[null,null,null,null,"Static Pressure:",null,null,null,null,null,null,"This Startup Sheet is for use only by a qualified heating installer/service technician.  Refer to the Installation and Operation Manual for your reference.  Have this unit serviced/inspected by a qualified service technician, at least annually.  Failure to comply with the above could result in severe personal injury, death, or substantial property damage."]
[null,null,null,null," Pressure Drop @ Ignition:"]
[null,null,null,null,"Hi-Fire Gas Pressure:"]
[null,null,null,null,"Low-Fire Gas Pressure:"]